## Sheet1
This sheet shows A/C compressor manufacturer data on efficiency gains when reducing liquid temperature.
Note there is a 30 degree drop in liquid temperature which is double what is accomplished with the precooling.
Piston Pump:
scroll pump |  |  | cr30k6-pfv | Condition 1 | condition 2 | Change:
evap temp | 45 | 45 | evaporator temp | 45 | 45 | 0
cond temp | 130 | 100 | condensor temp | 130 | 100 | 30
RG | 65 | 65 | RG | 65 | 65 | 0
liq | 115 | 85 | liquid temperature, Deg F | 115 | 85 | 30
but / hr | 34400 | 40500 | btu output / hr | 30000 | 39200 | 130.7%
w | 3060 | 2110 | Power Used (W) | 2750 | 2210 | 80.36%
amps | 14.1 | 10 | amps | 13 | 10.7
lbs / hr | 505 | 520 | refrigerant lbs / hr | 439 | 505 | 115%
EER btu / w | 11.2418 | 19.1943 | EER (btu / hr out / w in) | 10.9091 | 17.7376 | 162.6%
0.68954
1.7074
(3.415 btu / hr = 1 watt)
COP = EER / 3.415