## Sheet1
| SCHOOLHOUSE DEEP ENERGY RETROFIT - ANNUAL HEAT LOAD CALCULATION, SOLAR DESIGN AND ACTUAL THERMAL PERFORMANCE | [13 empty] | Revised: 1 Dec 2009
Iteration 408
Executive Summary - A 'deep energy retrofit' has been undertaken to a forty-six year-old dwelling (a converted two classroom school) bringing very serious thermal deficiencies to superior quality standards:
A. The thermal envelope now encloses a 1232 sq ft s.f. dwelling, a 780 sq ft home occupation, 263 sq ft of semi-heated storage, plus a 256 sq ft mudroom/solar heater.
Thermal Envelope: Insulation has been upgraded to about R40 on exterior walls, R10 on the floor, and over R50 over the ceiling. Total Net Area: 2531 sq ft. (TFA: 226.4 m2a)
Recently, as a dwelling, wall and ceiling insulation had been about R4 and R7 respectively; - originally as a school, wall and ceiling insulation had been about R1.8 and R4.5.
B. Primary Heating System: South and west facing passive solar gain windows (approx. 50% of space heating need), (Feb. clear sky max.: about 300k Btu/day),
mudroom operates as a passive solar heater, with high mass (steel and masonry) heat storage throughout the dwelling. All glazing Thermotech fibreglass:
- Three 89" x 72" & two 73"x72" hi perf. thermal triple pane windows and an oversize, double thermal triple pane sliding patio door facing east of south in the main dwelling area,
- Three clerestory windows & two double thermal pane sliding patio doors facing due south, plus a thermal pane double 'French' door facing west in the mudroom (west wing).
C. Secondary Heating Systems:
1. Hi-efficiency, wood fired, high mass 'Norbert Senf/Masonry Stove Builders Heat-Kit' (firebrick and stone) , masonry heater centred in the dwelling (max: 24 k Btu/hr net),
2. LP gas fired fireplace unit located in the Living Room (max: 33.1 k Btu/hr net),
3. 4,100 watts electric baseboard heating units distributed throughout dwelling ( max: 14k Btu/hr net - but as yet never used), and
4. HRV recoveries average 12.6 M Btu/winter, plus internal heat gains average 6.5 M Btu/winter.
D. Expected Thermal Performance: - Floor Area expanded by an additional 11% - but Passive Solar, with Deep Energy Retrofit Saves about 97% of Original Space Heating Need of the School !
[7 empty] | Winter Seasonal Thermal Load |  |  |  | Maximum System Heating Load (excluding all gain sources)
| Design Day (-5.8 degrees F) Thermal Loss: | [9 empty] | 20.9299 | k Btu/hr or | 6.1324 | kw typical max. or | 27.0808 | W/m2aTFA
| Total Annual Heating Load per Year: | [5 empty] | 59.8299 | M Btu
| Annual Heating Provisions: | [9 empty] | System Heating Capability (Max.)
|  | Passive Solar Windows (322 LOF EA2#3#5) and Doors: |  |  |  |  | 29.496 | M Btu | 49.2998 | % | 7.2 | k Btu/hr(Feb) |  | 6.4684 | k Btu/hr seasonal average
|  | Internal, Mass & HRV Gains: |  |  |  |  | 19.1056 | M Btu | 31.9332 | % | 4.8 | k Btu/hr(Feb) |  | 4.1898 | k Btu/hr seasonal average
|  |  | Total Expected Net Solar, Int. & HRV Gains: |  |  |  | 48.6016 | M Btu | 81.233 | %
|  | Wood Fired Masonry Heater in Studio: |  |  |  |  | 10.6669 | M Btu | 17.8287 | % | 24 | k Btu/hr
|  | Liquid Propane Fireplace in Living Room: |  |  |  |  | 0.44913 | Mbtu | 0.75068 | % | 33 | k Btu/hr
|  | 4.1kW Electric Baseboard Heating - dispersed: |  |  |  |  | 0.11228 | M Btu | 0.18767 | % | 14 | k Btu/hr
|  |  | Total Expected Net Purchased Heating: |  |  |  | 11.2283 | M Btu | 18.767 | % | 83 | k Btu/hr | (ie: capability is four times max. req't !! )
[7 empty] | 4.4806 | k Btu/yr/net sqft purchased net heat
[7 empty] | 0.62646 | Btu / yr / DD64.4F / net sqft purchased net heat
[7 empty] | 14.5281 | kWhr/ yr/TFA sq m, perhaps meeting European 'PassivHaus' (15 kWhr/yr TFA sq m) criteria for space heating requirements.
| Expected Heating System Performance Measures: | [11 empty] | Total Winter Net Purchased Heat:
|  | Design Day Thermal Loss/Outside-Inside Delta T: |  |  |  |  | 6648.8104 | Gross Heat Req't Btu/day/degree F |  |  |  |  | 1569.8848 | Net Purchased Heat: Btu / DegDay64F
|  | Design Day Thermal Loss/net floor area: |  |  |  |  | 200.4488 | Gross Heat Req't Btu/day/net sq ft |  |  |  |  | 23.5822 | Net Purchased Heat Btu/day/net sq ft
|  | Design Day Thermal Loss/Delta T per net floor area: |  |  |  |  | 2.6532 | Gross H Req'tBtu/day/degF/ net sqft
|  | Winter Total Thermal Loss per DegDayF per net floor area: |  |  |  |  | 3.3381 | Gross H Req't Btu/DegDay64F/net sq ft |  |  |  |  | 0.62646 | Net Purchased Heat Btu/DegDay64F/net sq ft
|  | Expected Cost of Gross Purchased Heat (2008/9 $): |  |  |  |  | 212.8137 | per average winter season |  |  |  |  | 0.084923 | per winter season per net sq ft
|  | Tot'l Expected Gross Firewood @ 94% of purchased heat: |  |  |  |  | 2326.8497 | lb / year or | 0.66633 | of one bush cord - sustainably harvested from the owner's small woodlot.
E. Expected Thermal Performance in the Event of Extended Hydro or Fuel Emergency:
With an annual purchased heating load of only 11 M Btu, and a massive interior heated mass storing 77 k Btu/deg F, heating emergencies of twelve consecutive days
of bitterly cold 'Design Day' weather with neither purchased fuel nor typical solar insolation are required before freeze-up and/or thaw damage might occur!
This 12 day period is 2.4 times more than the total expected average number of 'Design Days' occurring each winter! With typical January weather and typical solar insolation, but
no purchased heating fuel, the unoccupied dwelling may well take a month and a half to drop to freezing! The risk of damage arising from heating system failure is very low!
F. Effect of Weather Variability:
The installed heating provisions are not only fully adequate for typical year to year climate and weather variations, but are expected to handle the heating needs of the
75 year extreme recorded weather occurrence (ie: 65% additional heat load) - even without electricity!
G. Thermal Performance - Summary:
While flawed by construction completion difficulties, the first winter's total purchased space heating fuel cost was $ 275 for 14.4 M net Btu. However, after adjusting for
both (i) the actual slightly colder than average winter '09 weather and (ii) construction flaws, purchased net wintertime heating was about 10.6 M Btu versus an expected 11.8 M Btu!
Construction completed, in future years, the total cost of purchased heating is expected to range between $200 and $250 (@ 2009 fuel costs) depending upon weather conditions.
Total cost of purchased heating fuel is expected to be about 5% of the $ 4,000 heating cost of a new home of near identical size and style built to just meet current Code
requirements. The premium quality heating, insulation and window treatment has cost about an additional $75,000.00, but saves nearly $ 3,800 per year (2008-9 dollars).
Fluctuating energy costs may well reduce the nominal 20 year 'payback' period considerably - yet the facilities provide (i) worry free heating with emergency fuel redundancy,
(ii) a much higher than normal level of fire and personal safety, (iii) considerably lower than usual maintenance, plus (iv) attractive cooking and baking opportunities!
All of the winter space heating needs could easily be satisfied through normal suppertime cooking/meal preparation using the bake oven in the masonry heater.
Building Description: | Location: Greater Napanee, Ontario, Canada
Floors: SE BR, Den, Studio, Workshop, Mudroom, Utility Rm Floor 1.5" concrete pavers on 1.5" foam, else Hardwood over TG ply with 1.5" foam; 4.1kW electric baseboard heating.
Wall:Larsen Truss variation - R:46.3 / 7" R6.613/" Urethane in blocked 2x3 & 2x4 studs with 2x3 strapping, Ceiling R50 7.5" R6.613/" Urethane plus R0.85; Hydro Rates for winter 2008-2009. | [13 empty] | Average daily delta T: |  | 3.5 | deg F
[13 empty] | ie. a night set back from 70 to |  |  | 66.5 | deg F
Outside Design Day Temp F: | -5.8 | dec.F(Picton, Ontario) | [5 empty] | Infiltr'n AC/H | 0.030216 | (double that of CO test) |  |  | Mudroom operated as solar heater (unconditioned space).
Net Area: sq ft | 2505.9652 | sq ft | Sensible Heat Recovery: |  | 0.76 | via HRV |  | Vent'n AC/H: | 0.24569 | (equiv. 0.3ACH for 2.5m ceilings) |  |  | Workshop & utility room are unfinished/unconditioned space.
[13 empty] | Min.midwinter soil temp 5' under slab, deg F: |  |  |  | 57
Effective Wall R:(@ low temp.) | 40 |  | Ceiling R max: | 60.5 | 50.5 | min. | Perim.Ins R: | 22 |  | Perimeter Ins Width: ft |  | 3.5 | Well temperature @80ft:deg.F (14May'08), deg F: |  |  |  | 55.4
Wall R excluding Ins: R5.8 |  |  | Belt R Value: | 22 | for lower 1 ft |  | All windows in main dwelling: 322 LOF clr4, EA2 #3# 5 |  |  |  |  | 10.7636 | sq ft/sq m | 3413 | Btu/kWh
Basic 'Design Day' Heat Load Calculation
ROOMS | Mstr Bdrm | SE Bdrm | DenKitchen | Studio | Living | CentreHall | Workshop | Utility Rm | Dining | EnsuiteBath | Main Bath | Extras | Mudroom | Totals
Floor Finish | hardwood | paver | paver/hwood | paver | hardwood | hardwood | paver | paver | hardwood | slate | slate |  | concrete | (typically excludes Mudroom)
Room Height ft | 10.33 | 10.21 | 10.29 | 10.23 | 9.17 | 9.17 | 10.33 | 10.27 | 9.17 | 9.25 | 8.47 |  | 12.68
Room Length ft | 16.21 | 16.21 | 22.67 | 33.83 | 16.42 | 9.58 | 10.42 | 14.79 | 11.69 | 10.54 | 10.54 |  | 14
Room Width ft | 11.43 | 10.4 | 16.75 | 22.83 | 9.58 | 7.25 | 8.04 | 11.92 | 10.67 | 5.67 | 5.58 |  | 15.25
Doors & Glass sqft | 6.4167 | 73 | 57.1979 | 133.5 | 12.5 | 0 | 0 | 6.4167 | 6.4167 | 6.4167 | 0 |  | 177.2214 | 479.0859
Doors & Glass U | 0.19 | 0.17286 | 0.18333 | 0.1725 | 0.19 | 0 | 0 | 0.17 | 0.17 | 0.19 | 0 |  | 0.29
Exposed Wall Length ft | 26.875 | 29.76 | 16.75 | 57.365 | 9.58 | 0 | 8.04 | 27.835 | 24.495 | 8.54 | 0 | 0 | 48.83 | 258.07
Exposed Wall U | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0 | 0 | 0.037873
Ceiling U | 0.019055 | 0.019055 | 0.019055 | 0.019802 | 0.016005 | 0.016005 | 0.016319 | 0.016319 | 0.016005 | 0.016005 | 0.016005 | 0 | 0.015918
Floor R Value | 10.85 | 8.825 | 9.8375 | 8.3252 | 9.1937 | 10.85 | 8.825 | 8.825 | 10.85 | 9.97 | 9.97 | 5.04 | 9
Tot.U,R Floor + Soil R5.04 | 0.062933 | 0.072124 | 0.067216 | 0.074821 | 0.070256 | 0.062933 | 0.072124 | 0.072124 | 0.062933 | 0.066622 | 0.066622 | 0 | 0.071225
Perimeter Ins Width ft | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 0 | 3.5 | 3.5 | 3.5 | 3.5 | 0 | 0 | 3.5
Perimeter Ins U | 0.045455 | 0.045455 | 0.045455 | 0.045455 | 0.045455 | 0.0001 | 0.045455 | 0.045455 | 0.045455 | 0.045455 | 0.0001 | 0 | 0.045455
Indoor Temperature @4pm F | 69.5 | 70 | 71.5 | 72 | 70.5 | 70 | 63 | 62 | 70 | 69 | 70 |  | 62.5
Avg.Indoor Temperature F | 67.75 | 68.25 | 69.75 | 70.25 | 69.3333 | 68.8333 | 62.125 | 61.125 | 68.8333 | 68.125 | 69.125 |  | 55 | 68.5113
Interior Area: sq ft | 193.2703 | 170.374 | 384.6025 | 779.6589 | 162.0136 | 75.815 | 91.7768 | 171.4068 | 127.8823 | 59.7618 | 58.8132 | 0 | 230.59 | 2505.9652 | sq ft
Equiv.PassvfHaus-TFA: m2a | 17.9559 | 15.8287 | 35.7318 | 72.4348 | 15.052 | 7.0436 | 8.5266 | 9.5548 | 11.881 | 5.5522 | 5.4641 |  | 21.4231 | 226.4486 | sq m
Net Ext Gnd Belt Area | 26.875 | 29.76 | 16.75 | 57.365 | 9.58 | 0 | 8.04 | 27.835 | 24.495 | 8.54 | 0 | 0 | 48.83 | 258.07
Gross Ext Wall Area | 277.6187 | 303.8496 | 172.3575 | 586.8439 | 87.8486 | 0 | 83.0532 | 285.8655 | 224.6192 | 78.995 | 0 | 0 | 619.1644 | 2554.893
Net Ext Wall Area | 244.3271 | 201.0896 | 98.4096 | 395.9789 | 65.7686 | 0 | 75.0132 | 251.6138 | 193.7075 | 64.0383 | 0 | 0 | 393.113 | 1983.0597
Volume cu ft | 1996.4822 | 1739.5185 | 3957.5597 | 7975.9105 | 1485.6647 | 695.2235 | 948.0543 | 1760.3478 | 1172.6807 | 552.7966 | 498.1478 |  | 2923.8812 | 25706.2678
Wall Loss Btu/hr F | 6.1082 | 5.0272 | 2.4602 | 9.8995 | 1.6442 | 0 | 1.8753 | 6.2903 | 4.8427 | 1.601 | 0 | 0 | 14.8884 | 39.7487
Belt Loss Btu/hr F | 1.2216 | 1.3527 | 0.76136 | 2.6075 | 0.43545 | 0 | 0.36545 | 1.2652 | 1.1134 | 0.38818 | 0 |  | 2.2195 | 9.5109
Total Wall Loss Btu/hr F | 7.3298 | 6.38 | 3.2216 | 12.507 | 2.0797 | 0 | 2.2408 | 7.5556 | 5.9561 | 1.9891 | 0 |  | 17.1079 | 49.2596
Ceiling Loss Btu/hr F | 3.6827 | 3.2465 | 7.3286 | 15.4388 | 2.593 | 1.2134 | 1.4977 | 2.7971 | 2.0468 | 0.95649 | 0.94131 | 0 | 5.1389 | 41.7424
Door/Glass Loss Btu/hrF | 1.2192 | 12.6186 | 10.4863 | 23.0288 | 2.375 | 0 | 0 | 1.0908 | 1.0908 | 1.2192 | 0 | 0 | 51.3942 | 53.1286
Infiltration Loss Btu/hr F | 1.0859 | 0.94611 | 2.1525 | 4.338 | 0.80804 | 0.37812 | 0.51564 | 0.95743 | 0.63781 | 0.30066 | 0.27094 | 0 | 1.5903 | 12.3911
Ventilation Loss Btu/hr F | 8.8293 | 7.6929 | 17.502 | 35.2729 | 6.5703 | 3.0746 | 4.1927 | 7.785 | 5.1861 | 2.4447 | 2.203 | 0 | 12.9307 | 100.7536
Above-Gnd Loss Btu/hr F | 22.1469 | 30.884 | 40.691 | 90.5855 | 14.426 | 4.6661 | 8.4468 | 20.186 | 14.9176 | 6.9102 | 3.4153 |  | 88.162 | 257.2753
SlabPerimLoss Btu/hr/F | 4.2756 | 4.7345 | 2.6648 | 9.1262 | 1.5241 | 0 | 1.2791 | 4.4283 | 3.8969 | 1.3586 | 0 | 0 | 7.7684 | 33.2882
SlabPerimLoss Btu/hrmin | 55.5824 | 61.5491 | 34.642 | 118.6412 | 25.9095 | 0 | 21.7445 | 75.281 | 66.2478 | 23.0968 | 0 |  | 116.5261 | 482.6945
SlabPerimLoss Btu/hrmax | 123.9915 | 137.3018 | 77.2784 | 264.6612 | 47.2468 | 0 | 39.6518 | 137.2772 | 120.8049 | 42.1177 | 0 |  | 201.9786 | 990.3314
Slab Down Loss Btu/hr/F | 12.163 | 12.2881 | 25.8513 | 58.3349 | 11.3824 | 4.7712 | 6.6193 | 12.3626 | 8.048 | 3.9815 | 3.9183 |  | 16.4238 | 159.7205
Slab Down Loss: Btu/hr | 88.1819 | 116.7366 | 284.3641 | 670.8512 | 100.5446 | 39.7603 | 10.7564 | 7.7266 | 67.0664 | 30.3587 | 33.7951 |  | -61.5892 | 1450.1419
Max-Total Slab Loss Btu/hr | 212.1733 | 254.0384 | 361.6425 | 935.5125 | 147.7914 | 39.7603 | 50.4082 | 145.0038 | 187.8713 | 72.4764 | 33.7951 |  | 140.3894 | 2440.4733
Min-Total Slab Loss Btu/hr | 143.7642 | 178.2857 | 319.0062 | 789.4925 | 126.4542 | 39.7603 | 32.5009 | 83.0076 | 133.3143 | 53.4555 | 33.7951 |  | 54.9369 | 1932.8365
Design Day Loss Btu/hr | 1762.5762 | 2472.2388 | 3353.4903 | 7660.9419 | 1192.1449 | 378.6772 | 598.3094 | 1424.5799 | 1244.1088 | 559.9798 | 282.854 |  | 5193.4253 | 20929.9012 | Btu / hr
Design Day Loss kW | 0.51643 | 0.72436 | 0.98256 | 2.2446 | 0.3493 | 0.11095 | 0.1753 | 0.4174 | 0.36452 | 0.16407 | 0.082875 |  | 1.5217 | 6.1324 | 27.0808 | W / m2a TFA
% Loss by Room: | 8.4213 | 11.812 | 16.0225 | 36.6029 | 5.6959 | 1.8093 | 2.8586 | 6.8064 | 5.9442 | 2.6755 | 1.3514 |  |  |  | (excludes HRV & Int.
Gains & Mudroom)
THERMAL GAINS: Solar Gains, Internally Generated Gains, Net Thermal Mass Gains and Heat Recovery Ventilation Gains
Clearness Fctr: | 1 | September | October | November | December |  | January | February | March | April | May
No. of Days in Month: |  | 30 | 31 | 30 | 31 |  | 31 | 28 | 31 | 30 | 31
Approx.No. Heating Days |  | 5 | 12 | 28 | 31 |  | 31 | 28 | 28 | 20 | 7 |  | 190 | heating days typical per winter
% Sunshine Trenton, ON |  | 39.6 | 36.5 | 21.6 | 23.2 |  | 25.5 | 29.6 | 34.5 | 34.7 | 35.4
% Sunshine Kingston, ON |  | 43.3 | 42.8 | 30.4 | 27.1 |  | 33.1 | 40.4 | 38.2 | 43.8 | 48.6
% Sunshine K&T average: |  | 41.45 | 39.65 | 26 | 25.15 |  | 29.3 | 35 | 36.35 | 39.25 | 42
Equiv. Sun Hours/mon |  | 105.6975 | 98.332 | 54.6 | 46.779 |  | 59.0395 | 71.05 | 90.148 | 100.0875 | 117.18
Dispersed & Snow Factor: |  | 1 | 1 | 1 | 1.1 |  | 1.2 | 1.2 | 1 | 1 | 1 |  | 1.6 fctr for new/old snow 11 & 27 Jan '09 measurements
Ideal Insolation due south: | South | 1409 | 1570 | 1484 | 1391 |  | 1514 | 1634 | 1461 | 1093 | 841
| West | 758 | 571 | 377.5 | 303.5 |  | 384 | 594.5 | 803.5 | 957 | 1044.5
NRC Daily Insol'n (south): Btu/sqft day |  | 1015 | 1015 | 761 | 840 |  | 1031 | 1316 | 1268 | 983 | 888 |  | Btu/sqft day
Est. NRC Daily Ins (west):Btu/sqftday |  | 546.0397 | 369.1497 | 193.5832 | 183.2782 |  | 97.395 | 478.8017 | 697.3566 | 860.6871 | 1102.8728 |  | Btu/sqft day
Snow Fctr NRC In (south): Btu/sqft day: |  | 1015 | 1015 | 761 | 924 |  | 1237.2 | 1579.2 | 1268 | 983 | 888
Snow Fctr NRC In (west): Btu/sqft day: |  | 546.0397 | 369.1497 | 193.5832 | 201.606 |  | 116.874 | 574.5621 | 697.3566 | 860.6871 | 1102.8728
Ideal Insol'n (30 deg E of S) | South | 1335.3333 | 1374 | 1263 | 1178.1667 |  | 1287.8333 | 1428.3333 | 1391.8333 | 1197.6667 | 1023.1667
| West | 989.8333 | 874.5 | 692 | 607.6667 |  | 705.8333 | 913.5 | 1046.8333 | 1062.1667 | 1027.6667
Est.Sno NRC Insol'n(30 E of S-south): |  | 961.9328 | 888.2866 | 647.6705 | 782.6211 |  | 1052.3827 | 1380.4308 | 1207.9703 | 1077.133 | 1080.3472 |  | Btu/sqft day
Est.Sno NRC Insol'n (30 E of S-west): |  | 713.0453 | 565.3615 | 354.8598 | 444.0204 |  | 692.1456 | 1059.4364 | 908.5453 | 955.2697 | 1085.0987 |  | Btu/sqft day
Sunlit Glass 30 E of S:
Incident South Btu/day | 210.7387 | 202716.4852 | 187196.382 | 136489.246 | 164928.5727 |  | 221777.7771 | 290910.2227 | 254566.1175 | 226993.6177 | 227670.9822
Incident West Btu/day | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
South Wall Solar Recovery | Btu/day | 653685.952 | 603639.3393 | 440127.5142 | 531833.8614 |  | 715151.5933 | 938078.2512 | 820881.9069 | 731970.757 | 734155.0078
679.5547 | MBtu/mon | 19.6106 | 18.7128 | 13.2038 | 16.4868 |  | 22.1697 | 26.2662 | 25.4473 | 21.9591 | 22.7588
south wall loss M Btu/mon: |  | 0.037486 | 0.089966 | 0.20992 | 0.23241 |  | 0.23241 | 0.20992 | 0.20992 | 0.14994 | 0.23241 | 1.6044 | M Btu/yr
0.0074972 |  | thus recovery constrained to south wall loss during daytime!
Mudroom (due south):
South Glass SHGC: | 0.5466 |  | West Glass SHGC: |  | 0.39 |  | South Glass Adj. SHGC: |  | 0.68325 |  | West Glass Adj.SHGC: |  | 0.4875 | superheating effect
Sunlit Glass sqft South/day | 77.7066 | 78872.1962 | 78872.1962 | 59134.7205 | 65273.5417 |  | 80115.5017 | 102261.8819 | 98531.9653 | 76385.5851 | 69003.4583
West/day: | 18.375 | 10033.4803 | 6783.1254 | 3557.0917 | 3367.7372 |  | 1789.6328 | 8797.9815 | 12813.9276 | 15815.1255 | 20265.2872
MudRm South Net Gain Btu/day |  | 53889.6717 | 53889.6717 | 40403.9804 | 44598.349 |  | 54739.164 | 69870.7467 | 67322.2696 | 52190.6869 | 47146.826
MudRm West Net Gain Btu/day |  | 3913.0573 | 2314.7415 | 1040.4493 | 820.886 |  | 436.223 | 2573.4096 | 4372.7528 | 6167.8989 | 8891.3947
MudRm Tot'l Solar Gain M Btu/mon |  | 1.7341 | 1.7423 | 1.2433 | 1.408 |  | 1.7104 | 2.0284 | 2.2225 | 1.7508 | 1.7372
MudRm tree-less Gain M Btu/mon |  | 1.5954 | 1.6029 | 1.1439 | 1.2954 |  | 1.5736 | 1.8662 | 2.0447 | 1.6107 | 1.5982 | 14.3309 | M Btu/yr
Base MudRm Loss Btu/mon |  | 331595.1115 | 1027227.03 | 1707348.2134 | 2633683.5206 |  | 3136044.0187 | 2800785.4176 | 2337322.5509 | 1152796.3728 | 619539.6439
Base MudRm Loss M Btu/mon |  | 0.3316 | 1.0272 | 1.7073 | 2.6337 |  | 3.136 | 2.8008 | 2.3373 | 1.1528 | 0.61954 | 15.7463 | M Btu/yr
MudRm Gain conveyed to Main M Btu/mon |  | 1.2638 | 0.13889 | 0.078817 | 0.074667 |  | 0.092026 | 0.12827 | 0.15578 | 0.13705 | 0.97867 | 3.0479 | M Btu/yr | gain-loss difference method
MudRm Gain conveyed to Main M Btu/mon |  | 0.5575 | 0.45718 | 0.2245 | 0.18125 |  | 0.26143 | 0.36451 | 0.50521 | 0.66 | 0.94935 | 4.1609 | M Btu/yr | blower gain method
MudRm Gain conveyed to Main M Btu/mon |  | 0.91063 | 0.29804 | 0.15166 | 0.12796 |  | 0.17673 | 0.24639 | 0.33049 | 0.39853 | 0.96401 | 3.6044 | M Btu/yr | average of above methods
Main Building (S30E):
Glass SHGC & Tree Fctr: | 0.53431
Main Insolation M Btu/mon |  | 3.2494 | 3.1006 | 2.1878 | 2.7318 |  | 3.6734 | 4.3522 | 4.2165 | 3.6385 | 3.771 | 30.9212 | M Btu / yr | 0.025802
Main Bldg. Plus Mudroom Contribution:
Solar gain per sun hour k Btu/hr |  | 39.7123 | 35.478 | 46.6921 | 66.1014 |  | 69.1494 | 67.6775 | 52.7678 | 41.8333 | 42.3915 | total | usable
Total Net Solar Gain: M Btu |  | 4.1975 | 3.4886 | 2.5494 | 3.0922 |  | 4.0825 | 4.8085 | 4.7569 | 4.187 | 4.9674 | 36.13 | 29.496 | 49.2998 | % Solar Gain
Int'l Gener'd Gains M Btu/mon | 0.029214 | 0.87643 | 0.90565 | 0.87643 | 0.90565 | (75% of 2.1W / m2a day) | 0.90565 | 0.818 | 0.90565 | 0.87643 | 0.90565 | 7.9755 | 6.5111 | 10.8827 | % Internal Gain
Thermal Mass Gain: M Btu |  | 0.013408 | 0.039638 | 0.066089 | 0.098448 |  | 0.11448 | 0.1026 | 0.088032 | 0.045922 | 0.024287 | 0.5929 | 0.48403 | 0.80902 | % Mass Gain
Thermal Mass Loss: M Btu | 4.8 | -0.0027934 | -0.011051 | -0.02482 | -0.04533 |  | -0.06918 | -0.090554 | -0.10889 | -0.11846 | -0.12352 | -0.5946 | -0.48543 | -0.81134 | % Mass Loss
Heat Recovery Vent'n Gain: M Btu |  | 0.53203 | 1.2049 | 1.6002 | 2.3836 |  | 2.7718 | 2.4841 | 2.1314 | 1.4748 | 0.84601 | 15.4289 | 12.5959 | 21.0528 | % HRV Gain
TOTAL HEAT GAIN, M Btu: |  | 5.6166 | 5.6278 | 5.0672 | 6.4346 |  | 7.8053 | 8.1226 | 7.7731 | 6.4657 | 6.6199 | 59.5328 | 48.6016 | 81.233 | % Int&Solar Gains
HEATING SEASON
|  | September | October | November | December |  | January | February | March | April | May |  | Total
Bellville Degree DaysC/m |  | 88.3 | 270.2 | 442.8 | 665.7 |  | 777 | 674.5 | 576.1 | 338.6 | 143.6 | 46.9 | 4023.7
Kingston Degree DayC/m |  | 105.9 | 289 | 447.8 | 678.7 |  | 790.4 | 711.5 | 607.4 | 378.7 | 193.3 | 86.5 | 4289.2
Avg Degree Day F/mo |  | 174.78 | 503.28 | 801.54 | 1209.96 |  | 1410.66 | 1247.4 | 1065.15 | 645.57 | 303.21 | 120.06 | 7481.61
Approx.Napanee DD 64.4F: |  | 174.78 | 503.28 | 801.54 | 1209.96 |  | 1410.66 | 1247.4 | 1065.15 | 645.57 | 303.21 | 1 | 7361.55
Approx.Picton DD 64.4F: |  | 156.1 | 472.9 | 755.6 | 1169.6 |  | 1380.8 | 1236.6 | 1044.7 | 522.8 | 291.2 |  | 7152.3
Approx Napane DD@avgT | 3.6 | 195.3364 | 552.6154 | 916.6558 | 1337.4097 |  | 1538.1097 | 1362.5158 | 1180.2658 | 727.7956 | 331.989 |  | 8142.6932 | conservative assumption!
Approx.Picton DD@avgT | 4.1113 | 176.6564 | 522.2354 | 870.7158 | 1297.0497 |  | 1508.2497 | 1351.7158 | 1159.8158 | 605.0256 | 319.979 |  | 7811.4432 | conservative assumption!
Average Temperature F:Picton |  | 60.6 | 49.1 | 39.2 | 31.5 |  | 19.9 | 20.7 | 30.7 | 43.5 | 55.4 | 0
SEASONAL HEAT LOAD CALCULATION
Ground Temp 5' below slab F: |  | 62 | 61 | 60 | 59 |  | 57 | 56 | 55 | 56 | 58
Above Ground Heat Load | (Napanee) | 1206125.3433 | 3412182.2217 | 5659988.8114 | 8257978.0841 |  | 9497221.552 | 8412998.7398 | 7287676.7566 | 4493851.2101 | 2049901.0872 |  | 50277923.8061
Slab Periphery Load Btu | (Picton) | 5592.4145 | 114085.2567 | 465288.8902 | 681076.2 |  | 918833.7098 | 789648.9338 | 543582.6938 | 199729.0909 | 14540.2778 |  | 3732377.4676
Slab Down Load Btu |  | 523244.2851 | 659517.7968 | 753241.7731 | 897181.8677 |  | 1134845.9386 | 1132354.2991 | 1372510.0095 | 1213236.7491 | 1016013.9031 |  | 8702146.6221
Slab Heat Load Btu | (Napanee) | 528836.6997 | 773603.0535 | 1218530.6633 | 1578258.0677 |  | 2053679.6484 | 1922003.2329 | 1916092.7033 | 1412965.84 | 1030554.1809 |  | 12434524.0897
TOTAL HEAT LOAD M Btu | (Napanee) | 1.735 | 4.1858 | 6.8785 | 9.8362 |  | 11.5509 | 10.335 | 9.2038 | 5.9068 | 3.0805 |  | 62.7124
USABLE INT'L/SOLAR M Btu | (Napanee) | 1.735 | 4.1858 | 5.0672 | 6.4346 |  | 7.8053 | 8.1226 | 7.7731 | 5.9068 | 3.0805 |  | 50.1109
Avg. Int'l&Solar Gain, Btu.hr: | (Napanee) | 2409.6695 | 5626.0555 | 7037.8393 | 8648.6179 |  | 10490.9602 | 12087.2708 | 10447.7745 | 8203.9126 | 4140.3969 |  | 7676.9441
Max.Purchased Load Mbtu | (Napanee) | 0 | 0 | 1.8113 | 3.4017 |  | 3.7456 | 2.2124 | 1.4306 | 0 | 0 |  | 12.6015
AvgMaxPurch'dLoad Btu/hr | (Napanee) | 0 | 0 | 2515.66 | 4572.1296 |  | 5034.4446 | 3292.1964 | 1922.8834 | 0 | 0
Avg Purchased Load (Watts) Napanee |  | 0 | 0 | 737.0884 | 1339.634 |  | 1475.0923 | 964.6135 | 563.4048 | 0 | 0 |  | 1015.9666
Above Ground Heat Load | (Picton) | 1090783.6991 | 3224597.6848 | 5376327.4018 | 8008770.9771 |  | 9312847.8103 | 8346312.9926 | 7161406.0594 | 3735794.8047 | 1975744.0665 |  | 48232585.4964 | 80.6162 | % above ground loss
Slab Periphery Load Btu | (Picton) | 5592.4145 | 114085.2567 | 465288.8902 | 681076.2 |  | 918833.7098 | 789648.9338 | 543582.6938 | 199729.0909 | 14540.2778 |  | 3732377.4676
Slab Down Load Btu | (Picton) | 431245.29 | 564452.1684 | 661242.7779 | 802116.2393 |  | 1039780.3102 | 1046488.5703 | 1277444.3811 | 1121237.7539 | 920948.2748 |  | 7864955.7659
Slab Heat Load | (Picton) | 436837.7045 | 678537.4251 | 1126531.6681 | 1483192.4393 |  | 1958614.02 | 1836137.5041 | 1821027.0749 | 1320966.8448 | 935488.5526 |  | 11597333.2335 | 19.3838 | % slab loss
Total Heat Loss, M Btu: | (Picton) | 1.5276 | 3.9031 | 6.5029 | 9.492 |  | 11.2715 | 10.1825 | 8.9824 | 5.0568 | 2.9112 |  | 59.8299 | M Btu per Year
Usable Net Gains: M Btu: | (Picton) | 1.5276 | 3.9031 | 5.0672 | 6.4346 |  | 7.8053 | 8.1226 | 7.7731 | 5.0568 | 2.9112 |  | 48.6016 | 81.233 | % Usable Solar & Recoveries
Net Purchased Load, M Btu: (Picton) |  | 0 | 0 | 1.4356 | 3.0574 |  | 3.4662 | 2.0598 | 1.2093 | 0 | 0 |  | 11.2283 | 18.767 | % purchased heating
Max. Avg. Net Purchased Load kW | [6 empty] | 1.365 | [6 empty] | (less than a typical portable electric heater)
Avg. Net Purchased Fuel: Btu/hr |  | 0 | 0 | 1993.9094 | 4109.3975 |  | 4658.8541 | 3065.1853 | 1625.3883 | 0 | 0 |  |  | (local firewood is typically ~ 6300 Btu/lb)
At 94% Firewood, net lbs/week: |  | 0 | 0 | 49.9807 | 103.0089 |  | 116.7819 | 76.834 | 40.7431 | 0 | 0 |  | 1675.3318 | lb/yr or | 0.47867 | cords
At 94% Firewood, gross lbs/week: |  | 0 | 0 | 69.4176 | 143.0679 |  | 162.1971 | 106.7139 | 56.5876 | 0 | 0 |  | 2326.8497 | lb/yr or | 0.66481 | cords
| SIZING CONVENTIONAL BACKUP HEAT EQUIPMENT | [6 empty] | Design Day Heat Loss Btu/hr: |  |  |  |  | Annual Backup Heating Cost:
|  | Total Required Heat @ -5.8 F: | [5 empty] | 20929.9012 | Btu/hr net | 6.1324 | kWh net | Assuming purchased fuel is 94% wood, 6% propane & 0% elect.:
| 4.1k W Electric Baseboard @ 99% eff & duty cycle = |  |  |  |  | 50.3606 | % | 6976.6337 | Btu/hr net | 2.0441 | kWh net |  | electric: | 0 | @ 99% & $0.199/kWh (2008)
| 43,000 Btu Propane Fireplace @ 77% eff & duty cycle = |  |  |  |  | 42.1422 | % | 13953.2675 | Btu/hr net | 4.0883 | kWh net |  | propane: | 26.2427 | @ 77% & $0.65/litre (2008)
[13 empty] | wood: | 186.571 | "@ 72% & $280/22MBtu cord
|  | Note: LPG: 21,671 Btu/l is assumed, but sometimes can be 24,222 Btu/l. | [8 empty] | Total Estimated Space Heating Cost: |  |  | 212.8137 | (average expected cost)
Actual heating cost is likely to be quite variable from year to year as both heating
need and supply depend upon variable weather/solar recoveries.
SIZING SLAB OF CONCRETE PAVERS FOR FEBRUARY SUNNY DAY
|  | Heat Gain from one sunny day: M Btu | [9 empty] | 0.30053 | M Btu
|  | Heat Loss While Collecting Solar Gain (8:00am to 4:00pm): | [5 empty] | 0.32695 | M.Btu/day | Heat Loss for 8Hr: |  | 0.10898 | M Btu
|  | Net Heat Gain by 5:00pm that must be stored in the dwelling to prevent overheating, M Btu: | [9 empty] | 0.19155 | M Btu
|  | Heat Gain to be stored in steel ceiling 26.44 cuft @ 59.76 58.7 Btu/cuft (@ 75% efficiency): M Btu | [9 empty] | 0.03507 | M Btu
|  | Required Concrete Volume @ 28 Btu/cuft & with |  |  |  | 5.44 | degree F. temperature swing; cu ft: |  |  |  |  | 1027.3006 | cu.ft
|  | Volume of Useful Existing Exposed Concrete Walls 533cu ft (@ 80% efficiency), cu ft: | [9 empty] | 447.72 | cu.ft
|  | Equivalent Volume 1540 cuft of Non-Exposed Concrete Walls (@ 25% efficiency) cu ft: | [9 empty] | 385
|  | Equivalent Volume 49 cuft of Indirectly Exposed Concrete Walls (@ 55% efficiency) cu ft: | [9 empty] | 27
|  | Volume of Masonry Heater and topping slab 17,200 lb/140 lb/cuft (@ 50% efficiency), cuft: | [9 empty] | 61.4286
|  | Required Volume of Concrete Slab (@ 70% efficiency), cu ft: | [9 empty] | 151.6458
|  | Required Slab Thickness for Den, Studio, SE Bdrm, (1242 sq ft), inches: | [9 empty] | 1.4652
|  | Thickness of 20" by 20" x 1 1/2" patterned concrete paver slabs required: inches | [9 empty] | 1.5
|  | Prime Heat Storage Capacity (Readily Available for Daily Fluctuations) as a Percent of Total Heat Storage Capacity: | [9 empty] | 45.7286 | %
Tables 15 to 18 '93 ASHRAE |  | Interpolation of Seasonal Heat Gain Factors For 44 Degress Latitude and Building Angle 30 Degrees East of Due South
"Handbook of Fundamentals" |  | September | October | November | December |  | January | February | March | April | May
East 40 | NE (-45) | 291 | 152 | 75 | 56 |  | 73 | 152 | 302 | 501 | 666
East 40 | ENE (-22.5) | 534 | 351 | 198 | 146 |  | 199 | 361 | 563 | 758 | 893
| ENE (-22.5) | 534 | 351 | 198 | 146 |  | 199 | 361 | 563 | 758 | 893
East 48 | NE (-45) | 240 | 108 | 47 | 34 |  | 46 | 107 | 250 | 461 | 645
East 48 | ENE (-22.5) | 465 | 266 | 117 | 73 |  | 117 | 274 | 494 | 724 | 893
| ENE (-22.5) | 465 | 266 | 117 | 73 |  | 117 | 274 | 494 | 724 | 893
East 30N 44 (average): |  | 421.5 | 249 | 125.3333 | 88 |  | 125.1667 | 254.8333 | 444.3333 | 654.3333 | 813.8333
South 40 | SE (-45) | 1033 | 1006 | 887 | 822 |  | 904 | 1049 | 1087 | 994 | 881
South 40 | SSE (-22.5) | 925 | 974 | 914 | 867 |  | 932 | 1015 | 968 | 782 | 601
| SSE (-22.5) | 925 | 974 | 914 | 867 |  | 932 | 1015 | 968 | 782 | 601
| SSW PM | 396 | 493 | 551 | 557 |  | 561 | 508 | 403 | 296 | 247
| SSW PM | 396 | 493 | 551 | 557 |  | 561 | 508 | 403 | 296 | 247
| SW PM | 222 | 247 | 269 | 276 |  | 273 | 250 | 220 | 199 | 200
South 48 | SE (-45) | 1040 | 925 | 713 | 610 |  | 729 | 968 | 1100 | 1081 | 1007
South 48 | SSE (-22.5) | 963 | 925 | 760 | 665 |  | 776 | 967 | 1014 | 895 | 749
| SSE (-22.5) | 963 | 925 | 760 | 665 |  | 776 | 967 | 1014 | 895 | 749
| SSW PM | 453 | 513 | 502 | 468 |  | 512 | 531 | 465 | 370 | 316
| SSW PM | 453 | 513 | 502 | 468 |  | 512 | 531 | 465 | 370 | 316
| SW PM | 243 | 256 | 255 | 247 |  | 259 | 261 | 244 | 226 | 225
South 30E 44 (average): |  | 1335.3333 | 1374 | 1263 | 1178.1667 |  | 1287.8333 | 1428.3333 | 1391.8333 | 1197.6667 | 1023.1667
West 40 | ESE PM | 980 | 878 | 721 | 649 |  | 734 | 916 | 1035 | 1051 | 1025
West 40 | ESE PM | 980 | 878 | 721 | 649 |  | 734 | 916 | 1035 | 1051 | 1025
| SE PM | 1033 | 1006 | 887 | 822 |  | 904 | 1049 | 1087 | 994 | 881
West 48 | ESE PM | 953 | 780 | 555 | 458 |  | 567 | 816 | 1012 | 1098 | 1114
West 48 | ESE PM | 953 | 780 | 555 | 458 |  | 567 | 816 | 1012 | 1098 | 1114
| SE PM | 1040 | 925 | 713 | 610 |  | 729 | 968 | 1100 | 1081 | 1007
West 30S 44 (average) |  | 989.8333 | 874.5 | 692 | 607.6667 |  | 705.8333 | 913.5 | 1046.8333 | 1062.1667 | 1027.6667
| --------------- | --------------- | --------------- | --------------- | --------------- | --------------- | --------------- | --------------- | --------------- | --------------- | ---------------
South 40 | S | 672 | 791 | 798 | 775 |  | 813 | 821 | 694 | 488 | 358
South 48 | S | 737 | 779 | 686 | 616 |  | 701 | 813 | 767 | 605 | 483
Calc South 44 (average): | S | 1409 | 1570 | 1484 | 1391 |  | 1514 | 1634 | 1461 | 1093 | 841
West 40 | W | 787 | 623 | 445 | 374 |  | 452 | 648 | 832 | 957 | 1024
West 48 | W | 729 | 519 | 310 | 233 |  | 316 | 541 | 775 | 957 | 1065
Calc West 44 (average): | W | 758 | 571 | 377.5 | 303.5 |  | 384 | 594.5 | 803.5 | 957 | 1044.5
WHAT IS THE LIKELIHOOD THAT THE TEMPERATURE IN THE DWELLING MIGHT DROP TO LEVELS WHERE DAMAGE FROM PIPE FREEZING MIGHT OCCUR?
The solar storage sizing calculation of page 4 uses a conservative estimate of the mass of concrete and steel because that mass must be
located to be readily loaded on a daily basis with wintertime solar heat energy. A full day of solar heating may be not much greater than five hours.
However, the original steel ceiling and all the masonry walls are now within the insulated thermal envelope. This is a very significant mass! There are about 13k lbs of steel
in the ceiling, and about 287 k lbs masonry walls, and 29 k lbs of conc. flooring! The thermal storage of steel is 0.12 Btu/lb per degree F. The storage of concrete averages
0.2 Btu/ lb per deg. F. Thus the steel ceiling can store 1.56 k Btu per deg. F., and the walls and floors about 63.2 k Btu/deg.F.! The masonry heater and LP fireplace weigh
about 19 k lbs and store about 3.8 k Btu/ deg F. Including an additional 1.7 k Btu/ F for 9.5 k lbs of studs and drywall, and furnishing (~6.7k Btu/deg F), thus the total thermal
| storage capability is about : |  |  | 77 | k Btu/deg.F ! The total thermal storage capability of the typical North American home is reportedly 7k Btu/deg.F.
| This renovation provides: |  |  | 11 | times the thermal storage of a typical dwelling - and over 85% of this mass is reclaimed or recycled material!
Consider Newton's Law of Thermal Conduction to approximate the dwelling's thermal performance:
(ie: The rate of heat flow is proportional to temperature difference, thus interior temperature of a cooling mass decays as a logarithm function over time.)
| Worst case (Consecutive Design Day) Situation, heat load = |  |  |  | 178.9371 | Btu/hr-F | Ti = | 69.25 | degrees F, | To = | -5.8 | degrees F,
| Assuming no significant solar or other heat input, how many days will it take for temperature to drop to freezing? ie: time t at Temp.= | [11 empty] | 32 | deg F.
| thus RC constant = (heat storage) / (heat load) = |  |  |  | 430.3189 | hr, or = | 17.93 | days.
| T final = T outside + (T initial inside - T outside) exp (-t / RC) = |  |  |  |  | -5.8 | + | 75.05 | exp (-t / | 430.3189 | ) = | 32
| thus | 37.8 | = | 75.05 | exp (-t / | 430.3189 | )
| and thus | 0.50366 | = exp (-t / | 430.3189 | )
| taking natural logs, |  | ln of | 0.50366 | is | -0.68585 | thus | -0.68585 | = - t / | 430.3189
| thus t = | 295.1322 | hours, or | 12.2972 | consecutive days to drop to freezing worst case! |  |  |  |  | However, such severe weather averages only five days total per winter!
As a matter of comparison, our previous dwelling in Carleton Place would experience freeze-up in 10 hours under similar weather conditions!
Under consistant worst case (Design Day) situation (no sun & no purchased heat), It will take five days before the temperature drops
to an uncomfortable 50 degrees F.
69.25
| For Average January Situations, net heat load is: |  |  |  | 95.2309 | Btu/hr-F | Ti = | 69.25 | degrees F, | To = | 19.9 | degrees F,
| Assuming typical solar but no purchased heat input, how many days will it take for temperature to drop to freezing? ie. time t at Temp.= | [11 empty] | 32 | deg F.
| thus RC constant = (heat storage) / (heat load) = |  |  |  | 808.5609 | hr, or = | 33.69 | days!
| T final = T outside + (T initial inside - T outside) exp (-t / RC) = |  |  |  |  | 19.9 | + | 49.35 | exp (-t / | 808.5609 | ) = | 32
| thus | 12.1 | = | 49.35 | exp (-t / | 808.5609 | )
| and thus | 0.24519 | = exp (-t / | 808.5609 | )
| taking natural logs, |  | ln of | 0.24519 | is | -1.4057 | thus | -1.4057 | = - t / | 808.5609
| thus t = | 1136.6202 | hours, or | 47.3592 | consecutive days to drop to freezing with typical January weather! !
January is the worst month, after that weather improves, so in reality, with typical weather and insolation but no purchased fuel, the dwelling temperature is unlikely to fall below 41 F.!
Under average January weather and average solar insolation - but with no purchased fuel, one could coast sixteen and a half days for the interior temperature to
drop below 50 degrees F! This situation would only occur if there was no hydro and no propane, and no-one to stoke the masonry heater - a fairly unlikely situation.
Any one 'purchased fuel' heat source (electric baseboards, LP fireplace or wood fired masonry heater) plus typical solar can maintain the dwelling at
a mid-day temperature of about 68 - 70 degrees F. - under worse case 'design day' January conditions. The Jan. 1998 'Ice Storm' would have been no problem at all !!
Normal household routines (ie: occupancy and the cooking of some meals in the bake oven of the masonry heater) can easily satisfy wintertime heating needs!
From an insurance perspective, the risk of this dwelling suffering damage arising from wintertime heating system failure is extremely low!
RECOMMENDED 'DESIGN DAY' HEATING STRATEGY - outside temperature: minus 5.8 deg.F - (2.5% - typical worst case)
|  | Case 1: Normal Ocupancy |  |  |  | Case 2: Non-Occupied Emergency
|  | OCCUPIED @ Mid-day 70 deg F |  |  |  | NON-OCCUPIED, Temperature Maintained @ 50 deg F
HEAT REQUIRED for Design Day: |  | 20.9299 | k Btu/hr |  |  | 12 | k Btu/hr after five days ( to possibly 16.7 days) of coasting down to 50 degrees F.
(ie: Heat for first five days is provided solely by interior mass, assumes no solar !)
HEATING SYSTEM CAPABILITY:
Primary System: | Winter passive solar (five south windows plus |  |  |  |  | Winter passive solar (five south windows plus
| four patio doors, & insulated concrete pavers: |  |  |  |  | four patio doors, & insulated concrete pavers):
| 5 to 6 k Btu/hr mid-winter avg. |  |  |  |  | 5 to 6 k Btu/hr mid-winter avg.
Secondary Systems:
(normal) | Masonry Heater (Norbert Senf) in Studio 24kBtu/hr
| 4.1kW Electric Baseboards or 14k Btu/hr |  |  |  |  | 4.1kW Electric Baseboards or 14k Btu/hr
| Regency P40 LP fireplace in Liv Rm 33.2 k Btu/hr |  |  |  |  | Regency P40 LP fireplace in Living Room: 12-43 k Btu @ 77%=33.2 k Btu/hr max
| Internal Recoveries: 1.25 k Btu/hr |  |  |  |  | Internal Recoveries: 0.8 k Btu/hr
| HRV Recoveries: 3.6 k Btu/hr |  |  |  |  | HRV Recoveries: 2.1 k Btu/hr
(hydro emergency)
| Masonry Heater (Norbert Senf) in Studio 20kBtu/hr |  |  |  |  | Regency P40 LP fireplace in Liv Rm: 12 k Btu/hr (assuming no backup power)
| Regency P40 LP fireplace in Liv Rm 33.2 k Btu/hr |  |  |  |  | Contribution from existing concrete floor slab: 2k to 3k Btu/hr.
| (assuming minimal back-up power) |  |  |  |  | Internal Recoveries: 0.4 k Btu/hr (no back-up power)
Internal Recoveries: 0.8 k Btu/hr
Window and Door Input Parameters - all frames are fiberglass by Thermotech
|  | Window Properties | [5 empty] | Glass Properties |  | Area sqft
inputs: | fixed south window U: |  | 0.17 |  |  |  | fixed south window SHGC: |  | 0.59 | 158.6085 |  |  | 322LOF EA2, #3#5,argon
| fixed other window U: |  | 0.17 | [9 empty] | 322LOF EA2, #3#5,argon
| awning south window U: |  | 0.19 |  |  |  | awn.south window SHGC: |  | 0.61 | 19.0191 |  |  | 322LOF EA2, #3#5,argon
| awning other window U: |  | 0.19 | [9 empty] | 322LOF EA2, #3#5,argon
| Den patio sl3 door U: |  | 0.19 |  |  |  | Den patio sl3 door SHGC: |  | 0.48 | 33.1111 |  |  | 321AFG Tir #5, argon
| Avg. Main U: |  | 0.17495 |  |  |  | Avg. Main SHGC: |  | 0.57452 | 210.7387
| Mudrm patio sl2 doors U: |  | 0.27 |  |  |  | Mudrm sl2 doors SHGC: |  | 0.52 | 66.2222 |  |  | 211AFG TiR, #3, argon
| Mudrm clerestories U: |  | 0.3 |  |  |  | Mudrm clerestories SHGC |  | 0.7 | 11.4844 |  |  | 211AFG TiR, #3, argon
| French door U: |  | 0.19 |  |  |  | French Door SHGC: |  | 0.39 | 18.375 |  |  | 211AFG TiR, #2, argon plus storm
| Avg. Mudrm U: |  | 0.29 |  |  |  | Avg. South Mudrm SHGC: |  | 0.5466 | 77.7066
computes: | SE Bedroom Window U |  | 0.17286
| Studio Window U |  | 0.1725 |  |  |  | 2008/2009 Elect. Rate: $ 0.056 /kWh grossed up to $ 0.199 /kWhr : | [5 empty] | 0.058895 | per Net k Btu
[7 empty] | 2008/2009 Propane Rate: $ 0.65/l | [5 empty] | 0.038953 | per Net k Btu
| Den Doors & Trans. U: |  | 0.1842 |  |  |  | 2008/2009 Firewood Rate: $ 280.00 / 22 M Btu Cord | [5 empty] | 0.017677 | per Net k Btu
Proposed 2010 El.Rates: $0.088, 7-11& 5-8 winter,11-5 summer; $0.072, 11-5 & 8-10 winter,7-11 & 5-10 summer, else $0.04
U.S. NREL Weather Data For Comparison Purposes
|  | September | October | November | December |  | January | February | March | April | May |  | Totals
Massena Radiation | kWh/mm/day | 3.3 | 3.1 | 2.2 | 2.4 |  | 3.1 | 4 | 4.1 | 3.3 | 2.9 |  | 28.4
Rochester Radiation |  | 3.2 | 3 | 2 | 1.9 |  | 2.5 | 3.1 | 3.3 | 3.1 | 2.7 |  | 24.8
Syracuse Radiation |  | 3.2 | 3.1 | 2 | 2 |  | 2.7 | 3.3 | 3.5 | 3.1 | 2.7 |  | 25.6
Average NREL Rad'n |  | 3.2333 | 3.0667 | 2.0667 | 2.1 |  | 2.7667 | 3.4667 | 3.6333 | 3.1667 | 2.7667 |  | 26.2667
Avg. NREL Radiation * 317 | Btu/sqft/day | 1024.9667 | 972.1333 | 655.1333 | 665.7 |  | 877.0333 | 1098.9333 | 1151.7667 | 1003.8333 | 877.0333 |  | 8326.5333
NRC Canmet 2007 | Btu/sqft/day | 1014 | 1014 | 761 | 840 |  | 1030 | 1284 | 1284 | 983 | 903 |  | 9113
NRC Canmet 2008 | Btu/sqft/day | 1015 | 1015 | 761 | 840 |  | 1031 | 1316 | 1268 | 983 | 888 |  | 9117
| Testing and Analysis to Determine the Typical Rate of Infiltration of the Renovated Dwelling - 27 Apr'09 | [12 empty] | Test Data: 27 Apr'09
[14 empty] | P.M. | CO ppm
Infiltration severely degrades thermal performance. It degrades the controlling of ventilation and humidity, and often leads to moisture, mold and mildew problems. | [13 empty] | 5:32 | 157
Even for relatively small quantities of air leakage, inbound infiltrating air needs to be heated in winter - but much worse, due to temperature and dew point differences, the outbound | [13 empty] | 5:42 | 146
air tends to condense within the wall/ceiling cavities. | [13 empty] | 5:51 | 146 | to 148
[14 empty] | 6:04 | 146 | to 148
This renovation was undertaken in a manner thought to best control infiltration. This involved (i) selecting very high quality windows and doors, (ii) reducing the number and size of | [13 empty] | 6:22 | 146 | to 148
operating windows, (iii) attempting to ensure quality window and door instalation and sealing procedures were used, (iv) selecting the tightest form of insulation (spray-in-place urethane), | [13 empty] | 6:35 | 148 | to 149
(v) identifying the tightest design form for insulation placement (a variation of 'Larsen' truss), and (vi) reducing envelope penetrations to those essential. | [13 empty] | 6:45 | 148 | to 149
[14 empty] | 6:49 | 146 | to 148
A lot of effort was put into ensuring a tight building - but did we succeed? There were still major penitrations of the envelope ( LP fireplace co-axial vent, plumbing stack vent, HRV | [13 empty] | 6:57 | 149
inlets and outlets, the kitchen range vent, the dryer vent, the masonry heater's flue) - none that could be eliminated without serious implications. What was their combined implication? | [13 empty] | 7:07 | 149
The stability of the test data clearly
The usual infiltration test is the 'blower door' test were the building is depressurized and air change per hour is determined. To account for the depressurization, technicians | [13 empty] | confirms that very tight construction
typically divide the test result by an arbitrary 10 or 20. This in it-self is a possible error of 100%, and is hardly reassuring, especially since tests typically cost $ 500 to $ 1000 ! | [13 empty] | was indeed achieved!
With some effort and care, by using a carbon monoxide as a tracer gas, and a carbon monoxide sensor with digital readout, one can quite easily measure infiltration directly.
Simply close the windows and doors, deactivate the HRV, seal exhaust fans, dryer, and masonry heater, then rig several fans in the dwelling to stir up the air. If at all possible,
locate the CO sensor central to the dwelling and so oriented to be monitored through a window from outside (binoculars?). Then bring a potfull of glowing charcoal embers into the house.
Allow the CO concentration to rise to about 150 ppm (a not too hazardous level), then remove the embers from the house, and note the CO concentration exactly one and two hours later.
Consider: | Let L = Desired Air Leakage in cfm;
| If V = house air volume in cu ft, |  |  | then time constant Tc = V / 60 L in hours, or restated, L = V / (60 Tc) | [6 empty] | Test data for 27 Apr'09 reflect the reality that if CO concentration has been
| If Ic = initial concentration in ppm, Fc = final concentration in ppm, and t = time in hours, then: | [9 empty] | increasing rapidly, and the source is withdrawn, a rapid drop in CO will be
|  | Fc = Ic e^(-t/Tc) | [8 empty] | measured due to the time lag for uniform mixing throughout the house. (ie: not
|  | thus time constant Tc = |  | - t/ln(Fc/Ic) |  | inputting Ic from actual test (in ppm) >> |  |  | 152 | << | unlike the dynamic response of an underdamped step function). Thus the
| Input start t: | 5 | 32 | 5.5333 |  | inputting Fc from actual test (in ppm) >> |  |  | 149 | << | initial concentration is estimated from averaging the first two data points.
| Input end t: | 7 | 7 | 7.1167 |  | thus actual test time (in hours) >> |  |  | 1.5833 | <<
[6 empty] | inputting house volume V in cu ft >> |  |  | 22782.3866 | << | spreadsheed ref. O96-N96
[5 empty] | then (Fc/Ic) = |  | 0.98026
[5 empty] | then ln(Fc/100) |  | -0.019934 |  | Note: Restrict Ic to 150 ppm. CO is both toxic and dangerous.
|  | then time constant Tc = |  | 79.4279 | hours |  |  | Stay outdoors during CO build period, during test time, and ventilate until building is well below 50 ppm.
thus from L = V/60 Tc
| Leakage L = | 4.7805 | cfm or | 0.01259 | ACH air changes per hour @ 40 deg F. |  |  |  | Leakage tests (with sealed vent penetrations) are expected to average over the winter to be about 0.014 ACH.
| Leakage L = | 5.7366 | cfm or | 0.015108 | ACH air changes per hour @ -6 deg F. |  |  |  | For infiltration J69 - page 2 analysis (ie: vents unsealed) lets double this and round to 0.03 ACH.
Year One Thermal Performance Summary (Winter 2008-2009)
Winter 2008/09 Thermal Performance Summary:
A. | The thermal performance of the dwelling's first winter was quite close to the expected space heating need as predicted by this spreadsheet simulation model.
B. | At no time was it either necessary, nor desired to use electrical baseboard heat in any portion of the dwelling.
C. | The ambience and comfort of the sun exposed rooms was highly attractive, resulting in less use of the north wing, and thus less propane being used than originally anticipated.
D. | Early in the winter there were heating inefficiencies from (i) HRV problems requiring open windows during the heated period, (ii) flue damper problems, and (iii) wet firewood.
It was late in the winter when the significance of two 30" by 30" holes in the ceiling insulation was realized - this has now been corrected!
NRCan. data indicates Sep. to Nov.'09 was typical, but Dec. to Feb. averaged 0.7C below normal, with Mar. to May supposedly about 0.7C warmer than average (felt colder here).
When these in-efficiencies and actual weather are accounted for, the computed actual performance was marginally better than the model prediction.
Note that occupancy this first winter averaged only slightly over one person, and that in the future, occupancy will average slightly above two persons.
The net effect in the future will be a slight increase in propane usage for the kitchen range and electrical consumption, but little change in requirements for space heating energy.
E. | The mudroom-solarium was at no time 'heated'. Surprisingly, the temperature in the mudroom was very seldom uncomfortable for working and never dropped below 45F at night.
F. | The preliminary data suggests that the extensive interior mass creates a time delay effect, slightly reducing fall space heating requirements, but hindering springtime heating needs.
G. | Thermal performance is impressive! A quality level of exterior insulation, in conjunction with triple pane passive solar, supplemented by a double pane solar heater -
involving simply hard coat low E glazing - eliminates about 95% of the space heating need of a similarly styled, conventionnally designed, new dwelling.
However, this is a renovation of a 46 year old building, whose structure and solar orientation are far from ideal - and yet it saves over 97% of it's original space heating need!
H. | This project clearly demonstrates that even in a non-ideal situation, a 'back to basics' renovation involving simple systems can sometimes provide exemplary performance!
This is worthy of serious consideration - as throughout Canada, essentially all existing housing is overly dependent upon fossil fuels and very seriously thermally deficient!
YEAR ONE - PERFORMANCE DATA AND CALCULATIONS - 1st September 2008 to 31 August 2009 :
|  | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Winter Total | Jun-Aug | YEAR TOTAL
|  | see note 1 | see note 1 |  | see note 3 |  | see note 3 | see note 3
Purchased Space Heating Fuel: |  | Oct: see note 2
Actual Wood Burnt: lbs. |  | 0 | 159.7 | 271.1 | 832.3 | 606.1 | 508 | 390.6 | 195.5 | 0 | 2963.3 |  | 2963.3 | +-5lbs or : | 0.84858 | bush cord!
Gross Site Wood Heat Burnt:M Btu |  | 0 | 1.0061 | 1.7079 | 5.2435 | 3.8184 | 3.2004 | 2.4608 | 1.2316 | 0 | 18.6688 |  | 18.6688 | M Btu Site | 0.0063 | M Btu / lb
Gross Source Wood Ht. Burnt: M Btu |  | 0 | 0.20122 | 0.34159 | 1.0487 | 0.76369 | 0.64008 | 0.49216 | 0.24633 | 0 | 3.7338 |  | 3.7338 | M Btu Source | 0.2 | source fctr
Net Wood Heat: M Btu |  | 0 | 0.7244 | 1.2297 | 3.769 | 2.7493 | 2.3043 | 1.7718 | 0.88679 | 0 | 13.4352 |  | 13.4352 | M Btu @ 72% | 0.72 | efficiency
Estimated LP burnt: litres |  | 0 | 0 | 11 | 31.25 | 4.5 | 2 | 0 | 0 | 0 | 48.75 |  | 48.75 | litres of propane
Gross Site LP Heat: M Btu |  | 0 | 0 | 0.23838 | 0.67722 | 0.097519 | 0.043342 | 0 | 0 | 0 | 1.0565 |  | 1.0565 | M Btu Site LP | 21.671 | k Btu/L
Gross Source LP Heat: M Btu |  | 0 | 0 | 0.27438 | 0.77948 | 0.11224 | 0.049887 | 0 | 0 | 0 | 1.216 |  | 1.216 | M Btu Source LP | 1.151 | source fctr
Net LP Heat: M Btu |  | 0 | 0 | 0.18355 | 0.52146 | 0.07509 | 0.033373 | 0 | 0 | 0 | 0.81348 |  | 0.81348 | M Btu @ 77% | 0.77 | efficiency
Tot.Site Heat Purchased: M Btu |  | 0 | 1.0061 | 1.9463 | 5.9207 | 3.9159 | 3.2437 | 2.4608 | 1.2316 | 0 | 19.7253 |  | 19.7253 | M Btu
Gross Source Purchased Heating Fuel: M Btu 0 |  |  | 0.20122 | 0.61596 | 1.8282 | 0.87593 | 0.68997 | 0.49216 | 0.24633 | 0 | 4.9497 |  | 4.9497 | M Btu Source Heat Energy
Tot.Actual Net Heat Purchased: M Btu |  | 0 | 0.7244 | 1.4133 | 4.2905 | 2.8244 | 2.3377 | 1.7718 | 0.88679 | 0 | 14.2487 |  | 14.2487 | M Btu @ 72.3% overall site efficiency
Tot. Actual Net Heat Purchased:
less defect: HRV unusable; M Btu |  | 0 | -0.37412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.37412 |  | -0.37412 | HRV operable Nov.
less defect: no Damper on Masonry Htr; M Btu |  | 0 | -0.0564 | -0.12 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1764 |  | -0.1764 | Damper installed Dec.
less defect: wet wood; M Btu |  | 0 | -0.034047 | -0.061485 | 0 | 0 | 0 | 0 | 0 | 0 | -0.095532 |  | -0.095532 | Wet firewood Oct/Nov.
less defect: ceiling insulation 'holes': M Btu |  | -0.079495 | -0.11045 | -0.39182 | -0.58367 | -0.67871 | -0.60827 | -0.52192 | -0.27226 | -0.14399 | -3.3906 |  | -3.3906 | (see note 7) | 0.45 | k Btu*DD
Effective Net Purchased Fuel: M Btu |  | 0 | 0.14938 | 0.83996 | 3.7068 | 2.1456 | 1.7294 | 1.2498 | 0.61453 | 0 | 10.4355 |  | 10.4355 | effective actual net purchased fuel
Avg.Exp'd Net Purchased Fuel: M Btu |  | 0 | 0 | 1.4356 | 3.0574 | 3.4662 | 2.0598 | 1.2093 | 0 | 0 | 11.2283 |  | 11.2283 | modelled fuel need - average climate data
Winter'09 Exp'd Purchased Fuel:M Btu |  | 0 | 0 | 1.4356 | 3.3432 | 3.7581 | 2.3256 | 0.93606 | 0 | 0 | 11.7986 |  | 11.7986 | modelled fuel need-winter '09 adjusted (notes3,4)
Passive Solar Gain:
Expected Solar Gain: M Btu |  | 4.1975 | 3.4886 | 2.5494 | 3.0922 | 4.0825 | 4.8085 | 4.7569 | 4.187 | 4.9674 | 36.13 |  | 36.13 | M Btu
Expected Sun Hours per mon: |  | 105.6975 | 98.332 | 54.6 | 46.779 | 59.0395 | 71.05 | 90.148 | 100.0875 | 117.18 | 742.9135 |  | 742.9135 | hrs
Expected Solar Gain/SunHr: M Btu/hr |  | 0.039712 | 0.035478 | 0.046692 | 0.066101 | 0.069149 | 0.067678 | 0.052768 | 0.041833 | 0.042392 | 0.048633 |  | 0.048633 | M Btu/hr
Measured Sun Hours per mon: |  | est.106 | est.98 | 24.2 | 47.4 | 99.2 | 102.6 | 129.2 | 97.3 | 43 | 746.9 |  | 746.9 | measurement commenced Nov.
Useful Sun Hours per mon:(6 / day max.) |  | est.106 | est.98 | 24.2 | 46 | 91.6 | 97.2 | 128.7 | 96.9 | 43 | 731.6 |  | 731.6 | hrs
Approx. Actual Solar Gain: M Btu |  | est.1.03 | est.2.77 | 1.1299 | 3.1332 | 6.8596 | 6.5783 | 6.7912 | 4.0536 | 1.8228 | 34.1687 |  | 34.1687 | M Btu
Ratio Approx.Actual to Expected Solar Gain: |  |  |  | 0.44322 | 1.0133 | 1.6802 | 1.3681 | 1.4277 | 0.96815 | 0.36696 | 0.94572 |  | 0.94572 | close to expectations
Overall Electrical Consumption (incl. DHWH):
Site Electrical Consumption: kWH |  | 911/ 3 const.trlrs | 919/ 3 const.trlrs | 675/ 2 const.trlrs | 466/ 1const.trlr | 381 | 314 | 330 | 373 | 400 | 4769 | 1307 | 6076 | kWH Site Elect.
Electrical Consumption per day: kWH |  | 30.3667 | 29.6452 | 22.5 | 15.0323 | 12.2903 | 11.2143 | 10.6452 | 12.4333 | 12.9032 | 17.4689 | 14.2065 | 31.6754
Gross Source Electrical Consumption: kWH |  | 3065.515 | 3092.435 | 2271.375 | 1568.09 | 1282.065 | 1056.61 | 1110.45 | 1255.145 | 1346 | 16047.685 | 4398.055 | 20445.74 | kWH Source Elect. | 3.365 | source factor
Other Energy Consumption:
Est. Site Kitchen Range LP: kWh |  | 0 | 0 | 0 | 26.7894 | 26.7894 | 24.1968 | 26.7894 | 25.9252 | 26.7894 | 157.2795 | 79.5039 | 236.7835 | kWh | 0.1361 | litre/day LP
Gross Source Est. Kitchen Range LP: kWh |  | 0 | 0 | 0 | 30.8346 | 30.8346 | 27.8506 | 30.8346 | 29.8399 | 30.8346 | 181.0287 | 91.509 | 272.5378 | kWh | 1.151 | source factor
Total Gross Site Energy Usage: kWhr |  | 911 | 1213.7876 | 1245.264 | 2227.5414 | 1555.1522 | 1288.6047 | 1077.7914 | 759.7954 | 426.7894 | 10705.7261 | 7165.9505 | 17871.6767 | kWh
0.86417
Total Gross Source Energy Usage: kWh |  | 3065.515 | 3151.3925 | 2451.8504 | 2134.5755 | 1569.545 | 1286.619 | 1285.485 | 1357.1589 | 1376.8346 | 17678.9759 | 5939.8262 | 23618.8022 | kWh
Total Gross Source Energy Consumption: kWh/m2a |  | 13.5374 | 13.9166 | 10.8274 | 9.4263 | 6.9311 | 5.6817 | 5.6767 | 5.9932 | 6.0801 | 78.0706 | 26.2303 | 104.3009 | kWh/TFA sq m
Fall 2008 energy (particularly electrical) consumption data is not representative as it involved consumption by 5 to 9 additional construction workers living or working on-site.
Combining Dec 2008 to Aug 2009 data with Sep to Nov 2009 data, annual total source energy consumption for the dwelling is about 83 kWh / m2a TFA / yr. The PassivHaus Institute criteria is currently 120 kWh / m2a / yr.
Notations & Comments Regarding Year One Summary on Previous Page:
|  | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May
note 1: windows open for all of Sep & Oct for ventilation (construction off-gassing), HRV not operational until 1 Nov'08. |  | Apr: note 2: firewood was wet for all of Oct and half of Nov., also no damper, thus masonry heater was quite inefficient initially.
note 3: NRCan indicates that Dec'08, Jan & Feb'09 averaged 0.7C colder than average (tabulated for Gr.Lakes/St.Lawrence). |  | Apr: note 4: NRCan reported Mar. Apr & May'09 was 0.7C warmer than average -( but I doubt it).
note 5: Re: electrical consumption, includes three construction trailers until mid-Nov. |  | Apr: note 6: Re: electrical consumption, includes one construction trailer until mid-Dec.
note 7: owner was aware that a 30" x 30" hole existed in the insulation around masonry heater's chimney, |  | Apr: note 8: Page 4 references both Napanee and Picton. Building is in municipality of Greater Napanee for purposes of building code
however, it was late April that another 30"x30" hole was found to have been left by contractor - |  | Apr: and permits, but is physically close to Picton, which has a slightly milder winter. Early iterations focussed on Napanee (for
These affect a very large area of steel decking by conduction, and are thus very major thermal hemorages & have now (Fall'09) been corrected!! |  | Apr: legal approvals), later iterations (model refinements) were more tailored to the Picton climate (more realistic).
|  | const.fumes | wet firewood! | [5 empty] | ice-free:1Apr | seemed to be
Insolation Summary: |  | wndws opn | very cloudy! | very cloudy! | cloudy | very snowy, | typical? | quite cold, but | cloudy, | much cooler
Temperature Summary: |  |  | colder than typ. | colder than typ. | colder than typ. |  | typical? | early snow melt | chilly month | than typical
Cummulative Firewood Consumption: |  |  | 0.046cord burnt | 0.12cord burnt | 0.36cord burnt | 0.54cord burnt | 0.68cord burnt | 0.79cord burnt | 0.85cord burnt | 0.85cord burnt
Comparison of Picton Climate with that of Hanover PassHaus Experience:
|  | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May
Hanover, DE: Avg.Temp. C. |  | 14 | 9.5 | 5 | 2.5 | 1 | 1 | 3.5 | 7.5 | 13
Picton, ON: Avg.Tem. C. |  | 15.9 | 9.5 | 4 | -3 | -6.7 | -6.3 | -0.7 | 6.4 | 13
Hanover,DE: HDD 21.11C | 21.11 | 213.3 | 359.91 | 483.3 | 576.91 | 623.41 | 563.08 | 545.91 | 408.3 | 251.41 | 4025.53 | ~HDD C | approx.HDD based om monthly avg. temp.
Picton, ON: HDD 21.11C |  | 156.3 | 359.91 | 513.3 | 747.41 | 862.11 | 767.48 | 676.11 | 441.3 | 251.41 | 4775.33 | ~HDD C | approx.HDD based om monthly avg. temp.
[13 empty] | 18.6261 | % more heat req'd!
Hanover, DE: HDD21C-last3yr |  | 133 | 226 | 350 | 451 | 457 | 408 | 382 | 234 | 149 | 2790 | ~HDD C | approx.HDD based on last 3yr airport data
Trenton, ON: HDD21C-last 3yr |  | 100 | 266 | 445 | 632 | 740 | 700 | 600 | 333 | 193 | 4009 | ~HDD C | approx.HDD based on last 3yr airport data
[13 empty] | 43.6918 | % more heat req'd!
Bottom Line: | This is a ranch style house, converted from another use (ie: far from ideal) in a far worse climate, but preforms as well or better than 1/3 of the Hanover PassivHaus townhouse dwellings!
However, it won't satisfy the requirements for PassivHaus Certification because of the significant area dedicated to the insulated, but un-heated mudroom/solar heater and semi-heated storage
(ie: property is far too valuable in Europe, and attached multi-storey, high density complexes are essential). However, in North America, there are millions of existing single storey dwellings,
and this renovation proves that deep energy retrofits can be just as successful in all manners with the exception of the foorprint of the materials in our larger homes. While we should place
higher emphasis on the reduction of the footprint of our new housing, the existing housing stock need not be considered obsolete - but a resource worthy of significant energy efficient upgrade!
Gordon Scale, P.Eng. (retired); co-owner and primary designer
YEAR TWO - PERFORMANCE DATA AND CALCULATIONS - 1 September to 30 November 2009 (under construction):
|  | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Fall Tot. | Jun-Aug | Year Total
Purchased Space Heating Fuel:
1. Actual Wood Burnt: lbs. |  | 0 | 125.3 | 126.38 | 0 | 0 | 0 | 0 | 0 | 0 | 251.68 | 0 | 251.68 | +-5lbs or : | 0.072072 | bush cord!
Site Wood Heat Burnt: M Btu |  | 0 | 0.78939 | 0.79619 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5856 | 0 | 1.5856 | M Btu wood heat
Gross Source Wood Heat Burnt: M Btu |  | Sep: 0; Oct: 0.15788; Nov: 0.15924 |  |  |  |  | 0.2 | source fctr
Net Wood Heat: M Btu |  | 0 | 0.56836 | 0.57326 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1416 | 0 | 1.1416 | M Btu @ 72% | 0.72 | efficiency fctr
2. L. Propane burnt: litres |  | 0 | 0 | 0.28887 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28887 | 0 | 0.28887 | litres of propane
Site LP Heat: M Btu |  | 0 | 0 | 0.00626 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00626 | 0 | 0.00626 | M Btu Site | 21.671 | k Btu / Ltr
Gross Source LP Heat: M Btu |  | 0 | 0 | 0.0072053 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072053 | 0 | 0.0072053 | M Btu Source | 1.151 | source fctr
Net LP Heat: M Btu |  | 0 | 0 | 0.0048202 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048202 | 0 | 0.0048202 | M Btu @ 77% | 0.77 | efficiency fctr
3. Electrical Consumption: kWH |  | 0 | 8.84 | 27.42 | 0 | 0 | 0 | 0 | 0 | 0 | 36.26 | 0 | 36.26 | kWhr electr. Space Heat
Site Electrical Consumption: M Btu |  | 0 | 0.030171 | 0.093584 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12376 | 0 | 0.12376 | M Btu Site Elect. Space Heat
Gross Source Elect.Consumption: M Btu |  | 0 | 0.10153 | 0.31491 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41644 | 0 | 0.41644 | M Btu Srce El. Sp | 3.365 | source fctr
Net Elect. Consumption @ 99%: M Btu |  | 0 | 0.029869 | 0.092649 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12252 | 0 | 0.12252 | M Btu Net El Space | 0.99 | efficiency fctr
Tot. Site Heat Purchased: M Btu |  | 0 | 0.81956 | 0.89604 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7156 | 0 | 1.7156 | M Btu purchased site space heating fuel
Tot. Site Heat Purchased: kWhr |  | 0 | 240.1292 | 262.5369 | 0 | 0 | 0 | 0 | 0 | 0 | 502.6661 | 0 | 502.6661 | kWhr purchased site space heating fuel
Tot.Gross Source Heat Purchased: M Btu |  | 0 | 0.2594 | 0.48136 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74076 | 0 | 0.74076 | M Btu source purchased space heating fuel
Tot.Gross Source Heat Purchased: kWh |  | 0 | 76.0044 | 141.036 | 0 | 0 | 0 | 0 | 0 | 0 | 217.0404 | 0 | 217.0404 | kWhr Source | 3413 | Btu/kWh
Tot. Net Purchased Fuel: M Btu |  | 0 | 0.59823 | 0.67073 | 0 | 0 | 0 | 0 | 0 | 0 | 1.269 | 0 | 1.269 | M Btu actual net purchased fuel
Expected Net Purchased Fuel: M Btu |  | 0 | 0 | 1.4356 | 3.0574 | 3.4662 | 2.0598 | 1.2093 | 0 | 0 | 11.2283 | n/a | 11.2283 | modelled fuel need - average climate data
Winter'10 Exp'd Purchased Fuel:M Btu |  | 0 | 0 | 1.4356 | 3.0574 | 3.4662 | 2.0598 | 1.2093 | 0 | 0 | 11.2283 | n/a | 11.2283 | modelled fuel need-winter '10 NRCan adj
Purchased Fuel to '10 Model Need: % |  | Sep: same; Oct: over 0.8M Btu
Passive Solar Gain:
Expected Solar Gain: M Btu |  | 4.1975 | 3.4886 | 2.5494 | 3.0922 | 4.0825 | 4.8085 | 4.7569 | 4.187 | 4.9674 | 36.13 | n/a | 36.13 | M Btu Expected Solar Gain
Expected Sun Hours per mon: |  | 105.6975 | 98.332 | 54.6 | 46.779 | 59.0395 | 71.05 | 90.148 | 100.0875 | 117.18 | 742.9135 | n/a | 742.9135 | sun hours
Expected Solar Gain/SunHr: M Btu/hr |  | 0.039712 | 0.035478 | 0.046692 | 0.066101 | 0.069149 | 0.067678 | 0.052768 | 0.041833 | 0.042392 | 0.048633 | n/a | 0.048633 | M Btu/hr Exp.Solar Gain/hr
Measured Sun Hours per mon: |  | 57.4 | 52.7 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 197.3 | n/a | 197.3 | hrs, measured solar hours
Useful Sun Hours per mon:(6 / day max.) |  | 57.4 | 52.7 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 197.3 | n/a | 197.3 | hrs, usefull solar hrs
Approx. Actual Solar Gain: M Btu |  | 2.2795 | 1.8697 | 4.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2207 | n/a | 8.2207 | M Btu Solar Gain
Ratio Approx.Actual to Expected Solar Gain: |  | 0.54306 | 0.53594 | 1.5971 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22753 | n/a | 0.22753
Electrical Consumption (incl. DHWH):
Metered Electrical Consumption: kWHr |  | 357 | 384 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 1098 | 0 | 1098 | kWhr Tot. Electr.at Main Meter
Electrical Consumption per day: kWHrs/day |  | 11.9 | 12.3871 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0659 | 0 | 12.0659 | Kwhr/day Tot. Electr.
Site Non Space Ht. Electr. Used kWhr: |  | 357 | 375.16 | 329.58 | 0 | 0 | 0 | 0 | 0 | 0 | 1061.74 | 0 | 1061.74 | kWhr Plug & DHWH Electr.
Source Plug & DHWH Elect.Use kWhr |  | 1201.305 | 1262.4134 | 1109.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 3572.7551 | 0 | 3572.7551 | kWhr Source Plug & DHWH Electr.
Other Energy Consumption:
Est. Kitchen Range LP: litres |  | 4.0714 | 4.2071 | 5.13 | 5.301 | 5.301 | 4.788 | 5.301 | 5.13 | 5.301 | 44.5306 | 15.732 | 60.2626 | litres | 0.171 | litres/day expected
Site Kitchen Range LP: kWh |  | 25.8517 | 26.7134 | 32.5732 | 33.6589 | 33.6589 | 30.4016 | 33.6589 | 32.5732 | 33.6589 | 282.7489 | 99.8911 | 382.64 | kWhr
Source Kitchen Range LP: kWhr |  | 29.7553 | 30.7472 | 37.4917 | 38.7414 | 38.7414 | 34.9923 | 38.7414 | 37.4917 | 38.7414 | 325.444 | 114.9746 | 440.4186 | kWhr Source Kitchen Range LP
Total Household Energy Use
Total Site Energy Used: kWhr: |  | Sep: 382.8517; Oct: 642.0026; Nov: 624.6901 | 1649.5444 |  | 1649.5444 | kWhr
Total Gross Source Energy Used: kWhr |  | Sep: 1231.0603; Oct: 1369.165; Nov: 1287.5644 | 3887.7897 |  | 3887.7897 | kWhr Total Source Energy
Total Gross Source Energy Used per
TFA Square Metre Area: kWhr/m2a |  | Sep: 5.4364; Oct: 6.0462; Nov: 5.6859 | 17.1685 |  | 17.1685 | kWh/net sq m Tot. Source Energy per TFA