## Sheet1
|  |  |  | CB210 Differential Temperature Pump Controller Using 40k Thermistor Sensors | [10 empty] | As Built: Feb. 2013
Conversion of A to D Readings to Temperature (in C) and Derivation of Curve Fitting Case Ranges for Slope and Offset Parameters
Input data depicted in red.
|  |  |  | Manufacturer's | [7 empty] | Cases | Sensed | Linear | Estimator | Derived
Current Limiting |  |  |  | Specs. +- | Linearized | Slope = m | b | Model | Total | Divider | Sensor | A to D | Divider | Slope = m | b | Temp.
Resistor, Ohm: | 47000 |  | Y | X | Sensor | del Y/del X |  | Prediction | Resistance | Voltage | Power | Reading @ | voltage | del Y/del Vs | offset | Deg. C.
Switch R, Ohm: | 0 |  | nominal 40k @ 25C. |  | Resistance |  |  | Y=mX+b | Rt Ohm | V | ~ W | 204.6 | Vs |  |  | (accuracy
Voltage, V: | 6.125 | Deg.F. | Deg.C. | R Ohm | R OHM | [6 empty] | Div per V |  |  |  | check)
(via LM317T regulator
triggered by VN10K |  | 167 | 75 | 5863.53 | 5743.2594 |  |  | 74.5273 | 52743.2594 | 0.66696 | 7.7453e-05 | 136.4593 | 0.66696 |  |  | 73.6541
VMOSFET)
|  |  | 70 | 6948.54 | 6780.2791 | -0.0043657 | 99.6008 |  | 53780.2791 | 0.7722 |  | 157.9924 | 0.7722 |  |  | 69.6448
64.5273
|  | 149 | 65 | 8271.15 | 8033.832 |  |  | 64.5131 | 55033.832 | 0.89413 | 9.9512e-05 | 182.9383 | 0.89413 | -38.0951 | 99.0618 | 65
Parallel 'Linearizer'
Resistor, Ohm: | 280000
(two 560k in parallel) |  |  | 60 | 9891.16 | 9553.6711 | -0.0029695 | 88.3695 |  | 56553.6711 | 1.0347 |  | 211.7002 | 1.0347 |  |  | 59.6811
54.5131
|  | 131 | 55 | 11885.38 | 11401.4152 |  |  | 54.5027 | 58401.4152 | 1.1958 | 0.00012541 | 244.6511 | 1.1958 | -29.0659 | 89.7556 | 55
AREF Voltage (Volts): | 5
|  |  | 50 | 14353 | 13653.1308 | -0.0019997 | 77.302 |  | 60653.1308 | 1.3787 |  | 282.092 | 1.3787 |  |  | 49.7384
44.5027
|  | 113 | 45 | 17422.82 | 16402.2034 |  |  | 44.4993 | 63402.2034 | 1.5845 | 0.00015308 | 324.1974 | 1.5845 | -23.0248 | 81.4838 | 45
|  |  | 40 | 21263.07 | 19762.328 | -0.001339 | 66.4624 |  | 66762.328 | 1.8131 |  | 370.9525 | 1.8131 |  |  | 39.8204
34.4993
|  | 95 | 35 | 26094.9 | 23870.2834 |  |  | 34.508 | 70870.2834 | 2.063 | 0.0001783 | 422.0901 | 2.063 | -19.2865 | 74.788 | 35
|  |  | 30 | 32210.77 | 28887.5864 | -0.0008985 | 55.9554 |  | 75887.5864 | 2.3316 |  | 477.0372 | 2.3316 |  |  | 29.9278
24.508
|  | 77 | 25 | 40000 | 35000 |  |  | 24.5365 | 82000 | 2.6143 | 0.00019528 | 534.8918 | 2.6143 | -17.4268 | 70.5593 | 25
|  |  | 20 | 49984.4 | 42413.011 | -0.00061197 | 45.9555 |  | 89413.011 | 2.9054 |  | 594.4428 | 2.9054 |  |  | 20.0552
14.5365
|  | 59 | 15 | 62868.15 | 51340.6743 |  |  | 14.5954 | 98340.6743 | 3.1977 | 0.00019916 | 654.2445 | 3.1977 | -17.2952 | 70.3046 | 15
|  |  | 10 | 79608.47 | 61985.1129 | -0.00043171 | 36.7599 |  | 108985.1129 | 3.4836 |  | 712.7413 | 3.4836 |  |  | 10.1921
4.5954
|  | 41 | 5 | 101516.15 | 74504.1121 |  |  | 4.6959 | 121504.1121 | 3.7557 | 0.00018933 | 768.4241 | 3.7557 | -19.0777 | 76.6509 | 5
|  | 32 | 0 | 130400 | 88966.8616 | -0.00032469 | 28.8868 |  | 135966.8616 | 4.0078 |  | 819.9869 | 4.0078 |  |  | 0.19208
|  | 23 | -5 | 168775.79 | 105302.5191 |  |  | -5.3041 | 152302.5191 | 4.2348 | 0.00017031 | 866.4498 | 4.2348 |  |  | -4.1403
|  | -13 | -25 | 567963 | 187543.1357 |  |  |  | 234543.1357 | 4.8976 |  | 1002.0518 | 4.8976 |  |  | -16.7844
Record Low: -33 deg. C. |  | -30.1 | -34.5 | 1000000 | 218750 |  |  |  | 265750 | 5.0417 | calculated max. | 1031.541 |  | Temperature = m Vs + b
[11 empty] | not to exceed 5.5 V! |  |  |  | in Celsius
Note: Processor has a 10 bit A to D. Thus, with a 5 Volt reference, it has a nominal accuracy of (5 Volts / 1023 intervals) = | [9 empty] | 0.0048876 | Volts/div. |  | 265.337 | divisions between 30 and 60 deg.C.
With the 'hardware' inputs (red) now provided, the Yellow highlights the 'software' parameters for the processor firmware. | [13 empty] | (bigger numbers improve accuracy!)
Copyright: Gord Scale, Adolphustown Schoolhouse (2012). | [7 empty] | Notes: | The intent of this spreadsheet is to develop slope and offset values for 8 ranges of linear approximations.
Khanh master/slave variant of the “Build It Solar $1k Domestic Hot Water System”. | [8 empty] | If a different thermistor is used, one must replace column 'E', if a different voltage is used, replace 'B10'.
Current limiting resistor 'B8' is selected to maximize the precision of the useful temperature range.
Permission is granted to readers of “BuildItSolar” to use the circuit design, spreadsheet and | [8 empty] | The 280k linearizing resistor compensates for the highly non-linear resistance of thermistors under extreme cold.
software code to construct their own Differential Controller for a “BIS $ 1k Domestic Hot Water System”. | [8 empty] | This resistance prevents an over-voltage condition at the A to D inputs to the processor (must never be negative, nor over 5.5 Vdc.)
However, do so at your own risk. Please ensure compliance with all Codes and regulations for your area. | [8 empty] | If your wintertime record cold temperature is lower than -34.5 deg. C., replace the 280k with a larger resistor.
The collector sensor will likely dominate the design as it can often has a wide range from very hot (in the sun)
to very cold (night-time in winter).